## Sheet1
Deviation PRID | Deviation occurred at site | Deviation occurred at location | Deviation identified date | Deviation opened date | Deviation nature | What is normal | What was deviated | Immediate impact | Corrections taken | Investigation scope | Investigation findings | Cause identified | Root cause identified | Corrective action | Preventive action | Impact assessment
1345 | B1 | Park | 2025-01-03 | 2025-01-03 | Equipment Failure | Equipment temperature should be maintained between 25 to 30 Degrees C | Equipment temperature was 32 Degrees C | No impact to process and product as the equipment temperature exceeded was only for 3 minutes | Chlled water flow increased | Inspection of chilled water flow | Chlled water flow reduced | Chilled wate rline clogged by particulates | Chlled water preventive maintenance procedure do not has check point to frequently inspect strainer to ensure no clogging | Chilled water preventive maintenance procedure updated | For all chilled water systems this corrective action was extended to all chilled water systems across sites | No impact to process and product

## Sheet2
Deviation PRID
Deviation occurred at site
Deviation occurred at location
Deviation identified date
Deviation opened date
Deviation nature
What is normal
What was deviated
Immediate impact
Corrections taken
Investigation scope
Investigation findings
Cause identified
Root cause identified
Corrective action
Preventive action
Impact assessment