## Sheet1
col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20 | col_21 | col_22 | col_23 | col_24 | col_25 | col_26 | col_27 | col_28 | col_29 | col_30 | col_31 | col_32 | col_33 | col_34 | col_35 | col_36 | col_37 | col_38 | col_39 | col_40 | col_41 | col_42
Deviation PRID | Deviation occurred at site | Deviation occurred at location | Deviation identified date | Deviation opened date | Deviation nature | What is normal | What was deviated | Immediate impact | Corrections taken | Investigation scope | Investigation findings | Cause identified | Root cause identified | Corrective action | Preventive action | Impact assessment PRID-20240409-001 | ABC Pharma Pvt. Ltd. | Manufacturing Unit 3 | Clean Room B | 2025-04-05 | 2025-04-06 | Temperature excursion in raw material storage | Storage temperature should be maintained between 15°C and 25°C | Temperature recorded at 28°C for 6 hours | Possible degradation of raw materials | requiring quality assessment | Temperature restored to normal | impacted materials quarantined | Review of temperature logs | HVAC system function | and material stability | HVAC system malfunction due to clogged filters | delay in temperature alert response | Inadequate HVAC maintenance | Preventive maintenance schedule not followed properly | Replaced HVAC filters | restarted system | and revalidated temperature control | Implemented automated temperature alerts and revised maintenance schedule | No immediate risk to product quality | but additional testing required before batch release